Kerala State Information Technology Mission

Department of Electronics & Information Technology

Government of Kerala

“Saankethika”,Vrindavan Gardens

Pattom,Thiruvananthapuram 695 004, Kerala, India

Tel.+91 471 2525444

Email: admin.ksitm@kerala.gov.in

TENDER NOTICE

Kerala State IT Mission (hereinafter as referred to as KSITM) invites online bids under two-cover system from reputed and financial sound agencies / firms for undertaking a Non Comprehensive Annual Maintenance Contract (AMC) for Daikin Air Conditioners installed at Saankethika Building, Kerala State IT Mission, Pattom, Trivandrum for a period of one year on a contract basis.

SCOPE OF WORK

a. A DAIKIN VRV Air-conditioning System is installed at the Kerala State IT Mission (KSITM), Saankethika Building, Vrindavan Gardens, Pattom, Thiruvananthapuram – 695004.

b. The installation comprises approximately 129 indoor units, 21 outdoor units, and 6 fresh air units (FAUs).

c. The purpose of this Non-Comprehensive AMC is to ensure the smooth and efficient operation of the air-conditioning system through regular preventive maintenance and prompt repair services.

d. Under the Non-Comprehensive AMC, replacement of defective parts and consumables shall be carried out on a chargeable basis. The cost of such replacements shall be incurred only after prior approval, based on quotation submitted by the service provider.

e. The bidder shall be a Daikin-authorized dealer/service provider, having an established service setup in Kerala with adequate technical personnel, infrastructure, and experience in handling Daikin VRV systems. The bidder must ensure the use of

genuine Daikin spare parts and consumables only.

f. The firm must have a proven track record in servicing and maintaining Daikin VRV systems and adequate manpower, tools, and testing equipment to execute the AMC effectively.

g. Preventive Maintenance to be carried out four (4) times a year (once every quarter) or whenever requested, which shall includes detailed inspection, cleaning of filters and coils, checking refrigerant level, verification of electrical connections, testing compressor performance, and ensuring overall system efficiency.

h. Breakdown Maintenance: The contractor shall attend to all complaints immediately upon intimation, during office hours (Monday to Saturday). Maximum downtime: not to exceed 24 hours from the time of reporting. Replacement of defective parts (except those excluded under Non-Comprehensive AMC) shall be done promptly with prior approval from KSITM.

i. Gas Charging: The contractor shall check refrigerant levels during every preventive maintenance visit. Gas charging, if required, shall be carried out using genuine Daikin refrigerants, only after obtaining prior approval, based on quotations submitted by the service provider.

j. Standby Arrangement: During major repairs requiring workshop attention, the contractor shall provide a temporary standby unit at no additional cost to ensure uninterrupted cooling in critical areas.

k. All servicing and repair work shall be carried out in a manner that does not interfere with the normal operations of the office.

l. The contractor shall maintain a service history sheet/logbook for each unit, recording all preventive maintenance, breakdown calls, and parts replaced. A copy of the service report must be submitted along with each quarterly bill to KSITM.

m. The air-conditioning system will be handed over to the contractor on an “as-is-where-is” basis. The contractor shall inspect and verify the functional condition of all units at the time of taking over the AMC. Upon completion of the contract period, the entire system must be handed back in fully functional condition, matching the

inventory and in good working order.

n. The contractor shall ensure availability of service engineers during all working days from 9:30 AM to 6:00 PM (Monday to Saturday). Emergency support must be made available 24x7, including Sundays and holidays, without any additional cost in case of critical breakdowns.

o. The contractor shall deploy qualified and trained service personnel, equipped with necessary tools, testing instruments, and safety gear to perform maintenance activities as per Daikin’s service protocols.

p. The contractor shall be responsible for ensuring safety, cleanliness, and proper disposal of waste materials during and after maintenance activities.

q. The rates should be quoted for Non Comprehensive ANNUAL MAINTENANCE exclusive of GST and applicable GST rate to be shown separately. GST shall be paid as per prevailing Government norms/rates. The price quoted shall be firm and

final.

r. If the performance of the contractor is not satisfactory and he fails to attend the complaint to any of the works as contained in the scope of work, recovery of Rs. 1000/- per day will be made from their bills.

s. Bidder can visit KSITM office for verification of AC units with prior approval from Administrative Officer, KSITM upto 12:00 pm on 17.01.2026

1.1 Desirous companies/firm/agency can download tender documents w. e. f. 29.12.2025 10:00 am from